## Sheet1
Pipe Sizing Formulation Chart
Length |  | Flow |  |  | Pressure Drop |  | Operating Pressure |  | Pipe Size mm
Mtrs | Feet | Cfm | L/sec | L/min | PSI | Bar | PSI | Bar | (Internal Dia)
56 |  | 72.4 |  |  | 10 |  |  | 15 | 18.0208
7.54
Recommended Pipe Size
Maxair Pipe to use
Air 32
Maxair is rated to 16 Bar with a 2:1 saftey factor. Other pressure ratings are available with larger internal diameters and flow rates. Please contact UPG for more information.
Fittings
Where the system is complex and intensively uses fittings and changes of direction,
it is also possible to approximate the effect of pressure loss due to the fittings.
Select the blue box and then type in the value from the yellow box and push Enter
Fitting Type |  |  | Qty
Elbow 90˚ |  |  | 6
Elbow 45˚
Tee main direction
Tee
Ball Valve |  |  | 1
Added Mtrs: |  |  | 7.54
| Elbow 90˚ | 7.44 | 1.24 | 32
| Elbow 45˚ | 0 | 0.24
| Tee Run | 0 | 0.34
| Tee | 0 | 1.38
| Ball Valve | 0.1 | 0.1
Note on M5: Operating Pressure is the opperating pressure of the system.
Note on H5: This is the flow you require by adding up all your tools/machines. You may need to allow extra for any future extensions or add-ons.
Note on I5: This is the flow you require by adding up all your tools/machines. You may need to allow extra for any future extensions or add-ons.
Note on J5: This is the flow you require by adding up all your tools/machines. You may need to allow extra for any future extensions or add-ons.
Note on K5: Pressure Drop is the loss of pressure at end of the pipe. A pressure drop of 3-4% is generally acceptable.
Note on L5: Pressure Drop is the loss of pressure at end of the pipe. A pressure drop of 3-4% is generally acceptable.
Note on N5: Operating Pressure is the opperating pressure of the system.